## Overview
Version 2.0, April 2022
Financial Model Tool for Apparel Sector, Commercial and Industrial (C&I) Rooftop Solar Photovoltaic (PV) Projects in Vietnam
This financial model tool is provided as a toolkit for a preliminary financial study for prospective apparel sector C&I rooftop PV projects in Vietnam. The tool provides users with a project's preliminary, high-level financial analysis, to help a facility owner determine whether or not to explore procuring installation of onsite PV generation. However, these results are not intended to be definitive, and users should still find an experienced professional before releasing a formal RFP.
How to run the model
The model includes three worksheets. The Summary Dashboard (See Tab 1. below) is the main worksheet where users provide inputs and see the output results. The inputs on this main worksheet are broken into a number of categories in the Main Inputs table. Some input cells (colored Orange and Green, for drop-down menus) start blank and are based on the user's own individual site and situaiton. Other input cells (colored Pink), have inputs already entered but the user can change them if the pre-set numbers do not apply to the user's case. These pre-set inputs are specific to Vietnam's context, e.g., Vietnam's corporate tax/inflation rate, Vietnam's anticipated annual electricity price escalation, and Vietnam's solar industry costs (upfront down payments, O&M, insurance). The model is designed to assess outputs for three types of financial structures for Rooftop PV as shown in the Summary Scenarios table on Tab 1.: 1. CAPEX Self-Purchase - Capital Expenditure Self-Purchase: This option, also referred to as a "turnkey purchase," is for PV projects entirely financed by capital from the facility owner/electricity consumer's savings, who owns both the PV system and all the electricity it produces; 2. CAPEX Self-Purchase with Loan: This option is for PV projects financed with a loan secured by the facility owner/electricity consumer, who owns both the PV system and all the electricity it produces; and 3. OPEX - Operational Expenditure: This option, also referred to as a "Third-Party Power Purchase Agreement (PPA)," is when an entity other than the facility-owner/electricity consumer finances the PV system. The facility-owner/electricity consumer then only buys PV-generated electricity it needs from the third-party who retains ownership of the PV system. This tool estimates for a 20-year project lifetime and PPA contract length. All three financial structures above include the ability to incorporate a "Feed-in-Tariff" (FIT). However, currently in Vietnam, no FIT legally exists that would permit a facility owner to both consume PV electricity and export the excess to the EVN grid. The Financing (see Tab 2. below) worksheet shows the outputs of the financial model. This cannot be edited. The Sensitivity Analysis (see Tab 3. below) worksheet enables users to adjust specific inputs and see what the impact on critical outputs would be. Directions are located on the Sensitivity Analysis worksheet itself.
Legend
Text | Input data from Users | Text | Drop-down list, choose value
Text | NOT to edit | Text | Default values but can be changed by users
About Clean Energy Investment Accelerator (CEIA)
This financial model tool has been developed by the Clean Energy Investment Accelerator (CEIA). The CEIA brings together large commercial and industrial users to demonstrate innovative renewable energy purchasing models. The CEIA aggregates clean energy demand of multiple buyers to reach economies of scale, lower the cost of renewables, attract quality service providers, and drive investment toward new pools of projects. The CEIA is jointly led by Allotrope Partners, World Resources Institute (WRI), and the U.S. National Renewable Energy Laboratory (NREL). Please kindly contact us at info@cleanenergyinvest.org or visit our website for more information: www.cleanenergyinvest.org
Disclaimer
This tool is solely intended to provide a preliminary study and financial analysis of C&I rooftop PV projects in Vietnam. Therefore, the model has been designed as both simple and user-friendly. The financial model also reflect numerous assumptions in addition to those described in this communication, with respect to current general business, economic, market, and financial conditions and other policy matters in Vietnam as of April 2022. Accordingly, there can be no assurance that the assumptions made in this model in preparing the financial models will prove accurate to your business and power systems. The users are expected to observe differences between actual operation output and results provided this model. Neither CEIA Vietnam, nor any authors or contributors to toolkit development, in any way whatsoever, can be held responsible for the use of the information derived from this model.

## Tab 1. Summary Dashboard
MAIN INPUTS | [7 empty] | SUMMARY SCENARIOS
|  |  |  | * = See Guide Book for greater details | [5 empty] | VND | USD ($) | Euro (€)
| Tariffs |  |  |  | Market Data |  |  | No Rooftop Solar PV | Average annual electricity expense to EVN | 12185480109.2482 | 529803.483 | 468672.3119
| Standard hour (normal) |  | 1685 | VND/kWh | USD exchange rate | 23000 | VND/USD |  | Total 20-year electricity expense to EVN | 243709602184.9635 | 10596069.6602 | 9373446.2379
| Off-peak hour |  | 1100 | VND/kWh | EUR exchange rate | 26000 | VND/EUR |  | NPV | -92511837996.8615 | -4022253.826 | -3558147.6153
| Peak hour |  | 3076 | VND/kWh | Corporate tax | 20%
| Net-billing payment (FIT) |  | 0 | VND/kWh | Inflation rate | 4.5% |  | CAPEX Self-purchase | Total Upfront Cost | -12420000000 | -540000 | -477692.3077
| EVN tariff escalation |  | 3.6% | /year | Cost of debt* | 10.5% |  |  | Project IRR | 19.06% | 19.06% | 19.06%
[5 empty] | Risk free rate* | 6% |  |  | Average annual PV savings (expense) | 2725147572.4138 | 118484.6771 | 104813.3682
| Electricity Consumption |  |  |  | Market risk premium* | 8% |  |  | Total PV savings (expense) | 54502951448.2757 | 2369693.5412 | 2096267.3634
| Standard hour | (Mon-Sat) 4am - 9:30am, 11:30am - 5pm, 8pm - 10pm (Sunday) 4am - 10pm | 2170000 | kWh/year | Cost of equity* | 14% |  |  | NPV | 9436026765.5777 | 410262.0333 | 362924.1064
[5 empty] | WACC | 10.08% |  |  | Project payback period (years) | 5.4721 | 5.4721 | 5.4721
| Off-Peak hour | (Mon-Sun) 10pm - 4am | 725000 | kWh/year |  |  |  |  | LCOE - Levelized Cost of Energy (per kWh) | 1480.2938 | 0.064361 | 0.056934
| Peak hour | (Mon-Sat) 9:30am -11:30am, 5pm - 8pm | 1325000 | kWh/year | CAPEX Inputs
[5 empty] | Unit PV cost | 13800000 | VND/kWp | CAPEX Self-purchase with loan | Total Upfront Cost | -3726000000 | -162000 | -143307.6923
| Total Electricity Consumption |  | 4220000 | kWh/year | Total PV cost | 12420000000 | VND |  | Equity IRR | 27.76% | 27.76% | 27.76%
[5 empty] | Insurance cost | 0.25% | of total CAPEX/year |  | Average annual PV savings (expense) | 2009284461.7665 | 87360.194 | 77280.1716
| Rooftop & PV System Specifics |  |  |  | O&M | 115000 | VND/kWp/year |  | Total PV savings (expense) | 40185689235.3309 | 1747203.8798 | 1545603.4321
| Major City Nearest to Location of the roof (° lattitude) |  | Ho Chi Minh City (11° N) |  | Debt | 70% |  |  | NPV | 9968610504.8705 | 433417.848 | 383408.0963
| PV capacity to be installed on the roof |  | 900 | kWp | Equity | 30% |  |  | Project payback period (years) | 5.0227 | 5.0227 | 5.0227
| PV electricity exported to grid (in Net Billing) |  | 100% | % of consumable PV | Term | 8 | years
| PV output degradation (from panel aging) |  | 0.5% | /year | Amount of debt | 8694000000 | VND | OPEX / PPA Self-consumption | Upfront PV cost | 0 | 0 | 0
| PV system total output in year 1 |  | 1291680 | kWh/year | Amount of equity | 3726000000 | VND |  | Annual PV savings (expense) | 177859940.9563 | 7733.0409 | 6840.767
[9 empty] | Total PV savings (expense) | 3557198819.127 | 154660.8182 | 136815.3392
[5 empty] | OPEX Inputs |  |  |  | NPV - Net Present Value | 1371669391.1988 | 59637.7996 | 52756.515
[5 empty] | Price discount from EVN tariff | 5% |  |  | Project payback period | Day 1
[5 empty] | PPA net billing revenue retained* | 0%

## Tab 2. Financing
Electric Tariff | Rate |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Standard (normal) | 1685 | VND/kWh |  | No PV System
Off-Peak | 1100 | VND/kWh |  | Electric Consumed
Peak | 3076 | VND/kWh |  | Standard Hour (kWh) |  | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000
Net-Billing Payment | 0 | VND/kWh |  | Peak Hour (kWh) |  | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000
Peak Period for PV | 3076 | VND/kWh |  | Off Peak Hour (kWh) |  | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000
|  |  |  | Total (kWh) |  | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000
Installed Capacity | 900 | kWp
Standard PV Hours Portion of a Day | 0.75 |  |  | Retail Tariff
Peak PV Hours Portion of a Day | 0.25 |  |  | Standard Hour (VND/kWh) |  | 1685 | 1745.66 | 1808.5038 | 1873.6099 | 1941.0599 | 2010.938 | 2083.3318 | 2158.3317 | 2236.0317 | 2316.5288 | 2399.9238 | 2486.3211 | 2575.8287 | 2668.5585 | 2764.6266 | 2864.1531 | 2967.2627 | 3074.0841 | 3184.7511 | 3299.4022
PV System Output Year 1 | 1291680 | kWh/year |  | Peak Hour (VND/kWh) |  | 3076 | 3186.736 | 3301.4585 | 3420.311 | 3543.4422 | 3671.0061 | 3803.1623 | 3940.0762 | 4081.9189 | 4228.868 | 4381.1073 | 4538.8271 | 4702.2249 | 4871.505 | 5046.8792 | 5228.5668 | 5416.7952 | 5611.7998 | 5813.8246 | 6023.1223
PV Energy Consumed On-Site | 100% |  |  | Off Peak Hour (VND/kWh) |  | 1100 | 1139.6 | 1180.6256 | 1223.1281 | 1267.1607 | 1312.7785 | 1360.0385 | 1408.9999 | 1459.7239 | 1512.274 | 1566.7159 | 1623.1176 | 1681.5499 | 1742.0857 | 1804.8007 | 1869.7736 | 1937.0854 | 2006.8205 | 2079.066 | 2153.9124
EVN Tariff Escalation | 3.6%
CAPEX (per kWp) | 13800000 | VND/kWp |  | Electricity Expense
Total CAPEX | 12420000000 | VND |  | Standard Hour (VND) |  | 3656450000 | 3788082200 | 3924453159.2 | 4065733472.9312 | 4212099877.9567 | 4363735473.5632 | 4520829950.6114 | 4683579828.8335 | 4852188702.6715 | 5026867495.9676 | 5207834725.8225 | 5395316775.9521 | 5589548179.8863 | 5790771914.3623 | 5999239703.2793 | 6215212332.5974 | 6438959976.5709 | 6670762535.7274 | 6910909987.0136 | 7159702746.5461
PV Output Degradation | 0.5% | per year |  | Peak Hour (VND) |  | 4075700000 | 4222425200 | 4374432507.2 | 4531912077.4592 | 4695060912.2477 | 4864083105.0887 | 5039190096.8718 | 5220600940.3592 | 5408542574.2122 | 5603250106.8838 | 5804967110.7316 | 6013945926.718 | 6230447980.0798 | 6454744107.3627 | 6687114895.2277 | 6927851031.4559 | 7177253668.5883 | 7435634800.6575 | 7703317653.4812 | 7980637089.0065
Insurance Cost (of Total CAPEX) | 0.25% | per year |  | Off Peak Hour (VND) |  | 797500000 | 826210000 | 855953560 | 886767888.16 | 918691532.1338 | 951764427.2906 | 986027946.673 | 1021524952.7533 | 1058299851.0524 | 1096398645.6903 | 1135868996.9351 | 1176760280.8248 | 1219123650.9345 | 1263012102.3681 | 1308480538.0534 | 1355585837.4233 | 1404386927.5705 | 1454944856.9631 | 1507322871.8137 | 1561586495.199
O&M | 115000 | VND/kWp/year |  | Total Electricity Expense w/o RTS (VND) |  | 8529650000 | 8836717400 | 9154839226.4 | 9484413438.5504 | 9825852322.3382 | 10179583005.9424 | 10546047994.1563 | 10925705721.9459 | 11319031127.936 | 11726516248.5417 | 12148670833.4892 | 12586022983.4948 | 13039119810.9006 | 13508528124.093 | 13994835136.5604 | 14498649201.4766 | 15020600572.7297 | 15561342193.348 | 16121550512.3085 | 16701926330.7516
Inverter Replace | 1242000000 | VND/kWp
Inflation Rate | 4.5%
Corporate Tax | 20% |  |  | With PV System
|  |  |  | PV Energy Yield (kWh/year) |  | 1291680 | 1285221.6 | 1278795.492 | 1272401.5145 | 1266039.507 | 1259709.3094 | 1253410.7629 | 1247143.7091 | 1240907.9905 | 1234703.4506 | 1228529.9333 | 1222387.2837 | 1216275.3472 | 1210193.9705 | 1204143.0006 | 1198122.2856 | 1192131.6742 | 1186171.0158 | 1180240.1608 | 1174338.96
Debt | 70% |  |  | PV Energy for Self-Consumption (kWh/year) |  | 1291680 | 1285221.6 | 1278795.492 | 1272401.5145 | 1266039.507 | 1259709.3094 | 1253410.7629 | 1247143.7091 | 1240907.9905 | 1234703.4506 | 1228529.9333 | 1222387.2837 | 1216275.3472 | 1210193.9705 | 1204143.0006 | 1198122.2856 | 1192131.6742 | 1186171.0158 | 1180240.1608 | 1174338.96
Amount of Debt | 8694000000 | VND |  | Excess PV to EVN Grid (kWh/year) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Equity | 30%
Amount of Equity | 3726000000 | VND
Interest Rate | 10.5% |  |  | Electricity Savings and Revenue w/ PV System
Term | 8 |  |  | Standard Period Saved (VND) |  | 1632360600 | 1682669953.692 | 1734529841.6648 | 1787988051.3849 | 1843093843.1286 | 1899897995.3738 | 1958452851.5912 | 2018812368.4773 | 2081032165.6737 | 2145169577.0198 | 2211283703.3835 | 2279435467.1218 | 2349687668.2185 | 2422105042.153 | 2496754319.5522 | 2573704287.6808 | 2653025853.8271 | 2734792110.642 | 2819078403.492 | 2905962399.8877
|  |  |  | Peak Period Saved (VND) |  | 993301920 | 1023915485.1744 | 1055472560.4275 | 1088002224.7399 | 1121534453.3063 | 1156100145.1572 | 1191731151.631 | 1228460305.7242 | 1266321452.3467 | 1305349479.508 | 1345580350.4664 | 1387051136.8678 | 1429800052.9061 | 1473866490.5366 | 1519291055.775 | 1566115606.114 | 1614383289.0944 | 1664138582.0643 | 1715427333.1635 | 1768296803.5716
Cost of Equity | 14% |  |  | Net-billing Revenue (Untaxed) (VND) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk Free Rate | 6% |  |  | Electricity Savings and Revenue (VND) |  | 2625662520 | 2706585438.8664 | 2790002402.0923 | 2875990276.1247 | 2964628296.4349 | 3055998140.531 | 3150184003.2222 | 3247272674.2015 | 3347353618.0204 | 3450519056.5278 | 3556864053.85 | 3666486603.9896 | 3779487721.1246 | 3895971532.6897 | 4016045375.3271 | 4139819893.7947 | 4267409142.9215 | 4398930692.7063 | 4534505736.6555 | 4674259203.4593
Market Risk Premium | 8%
WACC | 10.08%
WACC (Sensitivity) | 10.08%
Operating Costs of PV System
Total CAPEX | 12420000000 | VND | % of Total Investment | Insurance Cost (VND) |  | -31050000 | -32447250 | -33907376.25 | -35433208.1812 | -37027702.5494 | -38693949.1641 | -40435176.8765 | -42254759.836 | -44156224.0286 | -46143254.1099 | -48219700.5448 | -50389587.0693 | -52657118.4874 | -55026688.8194 | -57502889.8162 | -60090519.858 | -62794593.2516 | -65620349.9479 | -68573265.6956 | -71659062.6519
PV Panel | 7017300000 | VND | 56.5% | O&M Cost (VND) |  | -103500000 | -108157500 | -113024587.5 | -118110693.9375 | -123425675.1647 | -128979830.5471 | -134783922.9217 | -140849199.4532 | -147187413.4286 | -153810847.0329 | -160732335.1494 | -167965290.2311 | -175523728.2915 | -183422296.0646 | -191676299.3875 | -200301732.8599 | -209315310.8386 | -218734499.8264 | -228577552.3186 | -238863542.1729
Inverter | 1242000000 | VND | 10% | Total Cost (VND) |  | -134550000 | -140604750 | -146931963.75 | -153543902.1187 | -160453377.7141 | -167673779.7112 | -175219099.7982 | -183103959.2892 | -191343637.4572 | -199954101.1427 | -208952035.6942 | -218354877.3004 | -228180846.7789 | -238448984.884 | -249179189.2037 | -260392252.7179 | -272109904.0902 | -284354849.7743 | -297150818.0141 | -310522604.8248
Civil Balance of Plant | 2235600000 | VND | 18%
Electrical Balance of Plant | 869400000 | VND | 7%
Grid Connection | 310500000 | VND | 2.5% | Net Electricity Expense Saved (VND) | -12420000000 | 2491112520 | 2565980688.8664 | 2643070438.3423 | 2722446374.006 | 2804174918.7208 | 2888324360.8198 | 2974964903.424 | 3064168714.9124 | 3156009980.5632 | 3250564955.3851 | 3347912018.1558 | 3448131726.6892 | 3551306874.3457 | 3657522547.8057 | 3766866186.1234 | 3879427641.0768 | 3995299238.8313 | 4114575842.932 | 4237354918.6414 | 4363736598.6345
Development Costs | 621000000 | VND | 5%
Other | 124200000 | VND | 1%
| 12420000000 | VND | 100% | Depreciation
|  |  |  | Initial Depreciation Expense (VND) |  | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -558900000 | -558900000 | -558900000 | -558900000 | -558900000 | -558900000 | -558900000 | -558900000 | -558900000 | -558900000 | -558900000
|  |  |  | Inverter Replacement Cost (VND) | [10 empty] | -124200000 | -124200000 | -124200000 | -124200000 | -124200000 | -124200000 | -124200000 | -124200000 | -124200000 | -124200000 | -124200000
PV Lease |  |  |  | Total Depreciation Expense (VND) |  | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000
Pricing Discount Below EVN | 5%
Net-Billing Revenue Retained | 0%
Debt
Emissions |  |  |  | Beginning Principal O/S (VND) | 8694000000 | 8694000000 | 7947452511.986 | 7122517537.7305 | 6210964391.1782 | 5203698164.2379 | 4090668983.4689 | 2860771738.7191 | 1501735283.2706 | 0 | 0
EVN Electricity Emission Factor (tCO2/kWh) | 0.0008458 |  |  | Interest Repayment (VND) | 0 | 912870000 | 834482513.7585 | 747864341.4617 | 652151261.0737 | 546388307.245 | 429520243.2642 | 300381032.5655 | 157682204.7434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Principal Repayment (VND) | 0 | 746547488.014 | 824934974.2555 | 911553146.5523 | 1007266226.9403 | 1113029180.769 | 1229897244.7498 | 1359036455.4485 | 1501735283.2706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Total Repayment (VND) | 0 | 1659417488.014 | 1659417488.014 | 1659417488.014 | 1659417488.014 | 1659417488.014 | 1659417488.014 | 1659417488.014 | 1659417488.014 | 0 | 0
|  |  |  | Ending Principal O/S (VND) | 8694000000 | 7947452511.986 | 7122517537.7305 | 6210964391.1782 | 5203698164.2379 | 4090668983.4689 | 2860771738.7191 | 1501735283.2706 | 0 | 0 | 0
Taxes
|  |  |  | Net Savings (VND) |  | 2491112520 | 2565980688.8664 | 2643070438.3423 | 2722446374.006 | 2804174918.7208 | 2888324360.8198 | 2974964903.424 | 3064168714.9124 | 3156009980.5632 | 3250564955.3851 | 3347912018.1558 | 3448131726.6892 | 3551306874.3457 | 3657522547.8057 | 3766866186.1234 | 3879427641.0768 | 3995299238.8313 | 4114575842.932 | 4237354918.6414 | 4363736598.6345
|  |  |  | Depreciation (VND) | 0 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000
|  |  |  | Interest (VND) | 0 | -912870000 | -834482513.7585 | -747864341.4617 | -652151261.0737 | -546388307.245 | -429520243.2642 | -300381032.5655 | -157682204.7434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Net Tax Payment (No Loan) (VND) | 0 | 361602504 | 376576137.7733 | 391994087.6685 | 407869274.8012 | 424214983.7442 | 441044872.164 | 458372980.6848 | 476213742.9825 | 494581996.1126 | 513492991.077 | 532962403.6312 | 553006345.3378 | 573641374.8691 | 594884509.5611 | 616753237.2247 | 639265528.2154 | 662439847.7663 | 686295168.5864 | 710850983.7283 | 736127319.7269
|  |  |  | Net Tax Payment (w/ Loan) (VND) |  | 179028504 | 209679635.0216 | 242421219.3761 | 277439022.5865 | 314937322.2952 | 355140823.5111 | 398296774.1717 | 444677302.0338 | 494581996.1126 | 513492991.077 | 532962403.6312 | 553006345.3378 | 573641374.8691 | 594884509.5611 | 616753237.2247 | 639265528.2154 | 662439847.7663 | 686295168.5864 | 710850983.7283 | 736127319.7269
Net Cash Flows
|  |  |  | Net Project Cash Flow (CAPEX, No Loan) (VND) | -12420000000 | 2129510016 | 2189404551.0931 | 2251076350.6738 | 2314577099.2048 | 2379959934.9767 | 2447279488.6558 | 2516591922.7392 | 2587954971.9299 | 2661427984.4506 | 2737071964.308 | 2814949614.5247 | 2895125381.3514 | 2977665499.4765 | 3062638038.2445 | 3150112948.8987 | 3240162112.8615 | 3332859391.065 | 3428280674.3456 | 3526503934.9131 | 3627609278.9076
|  |  |  | Accumulated Cash Flow (CAPEX, No Loan) (VND | -12420000000 | -10290489984 | -8101085432.9069 | -5850009082.2331 | -3535431983.0283 | -1155472048.0516 | 1291807440.6042 | 3808399363.3434 | 6396354335.2733 | 9057782319.7239 | 11794854284.0319 | 14609803898.5566 | 17504929279.908 | 20482594779.3845 | 23545232817.629 | 26695345766.5278 | 29935507879.3892 | 33268367270.4542 | 36696647944.7999 | 40223151879.713 | 43850761158.6206
|  |  |  | Net Cash Flow to Equity (CAPEX w/ Loan) (VND) | -3726000000 | 652666527.986 | 696883565.8308 | 741231730.9521 | 785589863.4055 | 829820108.4116 | 873766049.2947 | 917250641.2383 | 960073924.8646 | 2661427984.4506 | 2737071964.308 | 2814949614.5247 | 2895125381.3514 | 2977665499.4765 | 3062638038.2445 | 3150112948.8987 | 3240162112.8615 | 3332859391.065 | 3428280674.3456 | 3526503934.9131 | 3627609278.9076
|  |  |  | Accumulated Cash Flow (CAPEX, w/ Loan) (VND) | -3726000000 | -3073333472.014 | -2376449906.1832 | -1635218175.2311 | -849628311.8255 | -19808203.4139 | 853957845.8808 | 1771208487.1191 | 2731282411.9836 | 5392710396.4342 | 8129782360.7423 | 10944731975.2669 | 13839857356.6183 | 16817522856.0948 | 19880160894.3394 | 23030273843.2381 | 26270435956.0996 | 29603295347.1646 | 33031576021.5102 | 36558079956.4233 | 40185689235.3309
Payback and LCOE Calculations
|  |  |  | Payback Period (Self-Financed) (Year) | [6 empty] | 5.4721
|  |  |  | Payback Period (w/ Loan) (Year) | [6 empty] | 5.0227
|  |  |  | Total Annual Expense (VND) |  | 496152504 | 517180887.7733 | 538926051.4185 | 561413176.9199 | 584668361.4583 | 608718651.8752 | 633592080.483 | 659317702.2716 | 685925633.5698 | 713447092.2197 | 741914439.3253 | 771361222.6382 | 801822221.6481 | 833333494.4451 | 865932426.4284 | 899657780.9333 | 934549751.8565 | 970650018.3607 | 1008001801.7424 | 1046649924.5517
|  |  |  | Total Annual Expense, Discounted (VND) |  | 450719934.593 | 426801193.8177 | 404020977.4611 | 382339280.1688 | 361715807.738 | 342110248.1054 | 323482502.3145 | 305792880.0771 | 289002264.0608 | 273072246.6009 | 257965242.143 | 243644578.3716 | 230074568.6653 | 217220568.2294 | 205049016.0079 | 193527464.24 | 182624597.3253 | 172310241.4732 | 162555366.4461 | 153332080.5593
|  |  |  | Energy Yield (kWh) |  | 1291680 | 1285221.6 | 1278795.492 | 1272401.5145 | 1266039.507 | 1259709.3094 | 1253410.7629 | 1247143.7091 | 1240907.9905 | 1234703.4506 | 1228529.9333 | 1222387.2837 | 1216275.3472 | 1210193.9705 | 1204143.0006 | 1198122.2856 | 1192131.6742 | 1186171.0158 | 1180240.1608 | 1174338.96
|  |  |  | Sum of Discounted Annual Expenses (VND) |  | 5577361058.3985
|  |  |  | Initial Investment Cost (VND) |  | 12420000000
|  |  |  | Sum of Energy Yield (kWh) |  | 24642546.9678
|  |  |  | LCOE (VND/kWh) |  | 1480.2938
Leasing option (OPEX)
|  |  |  | PV Energy Yield (kWh/year) |  | 1291680 | 1285221.6 | 1278795.492 | 1272401.5145 | 1266039.507 | 1259709.3094 | 1253410.7629 | 1247143.7091 | 1240907.9905 | 1234703.4506 | 1228529.9333 | 1222387.2837 | 1216275.3472 | 1210193.9705 | 1204143.0006 | 1198122.2856 | 1192131.6742 | 1186171.0158 | 1180240.1608 | 1174338.96
|  |  |  | PV Energy for Self-Consumption (kWh) |  | 1291680 | 1285221.6 | 1278795.492 | 1272401.5145 | 1266039.507 | 1259709.3094 | 1253410.7629 | 1247143.7091 | 1240907.9905 | 1234703.4506 | 1228529.9333 | 1222387.2837 | 1216275.3472 | 1210193.9705 | 1204143.0006 | 1198122.2856 | 1192131.6742 | 1186171.0158 | 1180240.1608 | 1174338.96
|  |  |  | PV Energy during Peak Hour (kWh) |  | 322920 | 321305.4 | 319698.873 | 318100.3786 | 316509.8767 | 314927.3274 | 313352.6907 | 311785.9273 | 310226.9976 | 308675.8626 | 307132.4833 | 305596.8209 | 304068.8368 | 302548.4926 | 301035.7502 | 299530.5714 | 298032.9186 | 296542.754 | 295060.0402 | 293584.74
|  |  |  | PV Energy during Standard Hour (kWh) |  | 968760 | 963916.2 | 959096.619 | 954301.1359 | 949529.6302 | 944781.9821 | 940058.0722 | 935357.7818 | 930680.9929 | 926027.5879 | 921397.45 | 916790.4627 | 912206.5104 | 907645.4779 | 903107.2505 | 898591.7142 | 894098.7557 | 889628.2619 | 885180.1206 | 880754.22
Discount against EVN Offered by Developer
|  |  |  | PV Lease Standard Tariff (VND/kWh) |  | 1600.75 | 1658.377 | 1718.0786 | 1779.9294 | 1844.0069 | 1910.3911 | 1979.1652 | 2050.4151 | 2124.2301 | 2200.7024 | 2279.9276 | 2362.005 | 2447.0372 | 2535.1306 | 2626.3953 | 2720.9455 | 2818.8995 | 2920.3799 | 3025.5136 | 3134.4321
|  |  |  | PV Lease Peak Tariff (VND/kWh) |  | 2922.2 | 3027.3992 | 3136.3856 | 3249.2955 | 3366.2701 | 3487.4558 | 3613.0042 | 3743.0724 | 3877.823 | 4017.4246 | 4162.0519 | 4311.8858 | 4467.1136 | 4627.9297 | 4794.5352 | 4967.1385 | 5145.9555 | 5331.2099 | 5523.1334 | 5721.9662
PV energy during Peak Hour (kWh)
|  |  |  | Peak Period Expense Saved (VND) |  | 49665096 | 51195774.2587 | 52773628.0214 | 54400111.237 | 56076722.6653 | 57805007.2579 | 59586557.5815 | 61423015.2862 | 63316072.6173 | 65267473.9754 | 67279017.5233 | 69352556.8434 | 71490002.6453 | 73693324.5268 | 75964552.7887 | 78305780.3057 | 80719164.4547 | 83206929.1032 | 85771366.6582 | 88414840.1786
|  |  |  | Standard Period Expense Saved (VND) |  | 81618030 | 84133497.6846 | 86726492.0832 | 89399402.5692 | 92154692.1564 | 94994899.7687 | 97922642.5796 | 100940618.4239 | 104051608.2837 | 107258478.851 | 110564185.1692 | 113971773.3561 | 117484383.4109 | 121105252.1077 | 124837715.9776 | 128685214.384 | 132651292.6914 | 136739605.5321 | 140953920.1746 | 145298119.9944
|  |  |  | Net-Billing with Profit Sharing (VND) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Total Electricity Expense Saved (VND) |  | 131283126 | 135329271.9433 | 139500120.1046 | 143799513.8062 | 148231414.8217 | 152799907.0266 | 157509200.1611 | 162363633.7101 | 167367680.901 | 172525952.8264 | 177843202.6925 | 183324330.1995 | 188974386.0562 | 194798576.6345 | 200802268.7664 | 206990994.6897 | 213370457.1461 | 219946534.6353 | 226725286.8328 | 233712960.173
|  |  |  | Cumulative Electricity Expense Saved (VND) | 0 | 131283126 | 266612397.9433 | 406112518.0479 | 549912031.8542 | 698143446.6759 | 850943353.7025 | 1008452553.8636 | 1170816187.5737 | 1338183868.4747 | 1510709821.3011 | 1688553023.9936 | 1871877354.193 | 2060851740.2493 | 2255650316.8838 | 2456452585.6501 | 2663443580.3399 | 2876814037.4859 | 3096760572.1212 | 3323485858.954 | 3557198819.127
|  |  |  | Emissions Reductions | Total
|  |  |  | Total Electricity Consumption (kWh) | 84400000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000
|  |  |  | PV Energy for Self-Consumption (kWh/year) | 24642546.9678 | 1291680 | 1285221.6 | 1278795.492 | 1272401.5145 | 1266039.507 | 1259709.3094 | 1253410.7629 | 1247143.7091 | 1240907.9905 | 1234703.4506 | 1228529.9333 | 1222387.2837 | 1216275.3472 | 1210193.9705 | 1204143.0006 | 1198122.2856 | 1192131.6742 | 1186171.0158 | 1180240.1608 | 1174338.96
|  |  |  | Total EVN Electricity Consumption w/ PV (kWh) | 59757453.0322 | 2928320 | 2934778.4 | 2941204.508 | 2947598.4855 | 2953960.493 | 2960290.6906 | 2966589.2371 | 2972856.2909 | 2979092.0095 | 2985296.5494 | 2991470.0667 | 2997612.7163 | 3003724.6528 | 3009806.0295 | 3015856.9994 | 3021877.7144 | 3027868.3258 | 3033828.9842 | 3039759.8392 | 3045661.04
|  |  |  | Emissions without PV (tCO2) | 71385.52
|  |  |  | Emissions with PV (tCO2) | 50542.8538
|  |  |  | Emissions Reductions (tCO2) | 20842.6662

## Tab 3. Sensitivity Analysis
Key Paramater | Variable | [8 empty] | Variable | 0 | 1 | 2
WACC (Discount Rate) | Keep Original WACC rate | [8 empty] | 0 | No Change | Up 10% | Down 10%
Unit PV Cost (CAPEX) | Keep Original PV Unit Cost | Table 1- BASE CASE (Left bars of Figure 1, blue on Figure 2, does not change) |  |  |  | Table 2- SENSITIVITY ANALYSIS CASE (Right bars of Figure 1, orange on Figure 2, changes with "Variable" column) |  |  |  | 0 | No Change | Up 10% | Down 10%
Tariff Rates | Keep Original Tariff Rates | Net Present Value (NPV) | VND | USD ($) | Euro (€) | Net Present Value (NPV) | VND | USD ($) | Euro (€) | 0 | No Change | Up 10% | Down 10%
Price Discount from EVN Tariff (OPEX) | Keep Original savings % off EVN Tariff Rates | CAPEX Self-purchase NPV (Figure 1, orange) | 9436026765.5777 | 410262.0333 | 362924.1064 | CAPEX Self-purchase NPV (Figure 1, orange) | 9436026765.5777 | 410262.0333 | 362924.1064 | 0 | No Change | Up 10% | Down 10%
|  | CAPEX Self-purchase with loan NPV (Figure 1, blue) | 9968610504.8705 | 433417.848 | 383408.0963 | CAPEX Self-purchase with loan NPV (Figure 1, blue) | 9968610504.8705 | 433417.848 | 383408.0963
|  | OPEX/PPA NPV (Figure 1, grey) | 1371669391.1988 | 59637.7996 | 52756.515 | OPEX/PPA NPV (Figure 1, grey) | 1371669391.1988 | 59637.7996 | 52756.515
|  | OPEX/PPA Total PV Savings (Figure 2, blue) | 3557198819.127 | 154660.8182 | 136815.3392 | OPEX/PPA Total PV Savings (Figure 2, orange) | 3557198819.127 | 154660.8182 | 136815.3392
Simple Sensitivity Analysis Directions:
This sheet allows the user to change key inputs and see immediately how they affect signficant outputs, such as how they impact the NPV for each of the three models and the total PV savings for the OPEX model compared to the base case.
By selecting a different answer from the drop-down menus in the "Variable" column, for each "Key Parameter" to the variable's left, the model will display in both the table and the graphics in the boxed area to the right how such input changes impact the project's outcomes. Specifically, the sensitivity analysis case will change figures in Table 2, the right bars of Figure 1, and the orange line in Figure 2 (note that this line will not show up when there are no changes to the variables).

## Tab 4. Summary Dash Sensitivity (hidden)
MAIN INPUTS | [7 empty] | SUMMARY SCENARIOS
|  |  |  | * = See Guide Book for greater details | [5 empty] | VND | USD ($) | Euro (€)
| Tariffs |  |  |  | Market Data |  |  | No Rooftop Solar PV | Average annual electricity expense to EVN | 12185480109.2482 | 529803.483 | 468672.3119
| Standard hour (normal) |  | 1685 | VND/kWh | USD exchange rate | 23000 | VND/USD |  | Total 20-year electricity expense to EVN | 243709602184.9635 | 10596069.6602 | 9373446.2379
| Off-peak hour |  | 1100 | VND/kWh | EUR exchange rate | 26000 | VND/EUR |  | NPV | -92511837996.8615 | -4022253.826 | -3558147.6153
| Peak hour |  | 3076 | VND/kWh | Corporate tax | 20%
| Net-billing payment (FIT) |  | 0 | VND/kWh | Inflation rate | 4.5% |  | CAPEX Self-purchase | Total Upfront Cost | -12420000000 | -540000 | -477692.3077
| EVN tariff escalation |  | 3.6% | /year | Cost of debt* | 10.5% |  |  | Project IRR | 19.06% | 19.06% | 19.06%
[5 empty] | Risk free rate* | 6% |  |  | Average annual PV savings (expense) | 2725147572.4138 | 118484.6771 | 104813.3682
| Electricity Consumption |  |  |  | Market risk premium* | 8% |  |  | Total PV savings (expense) | 54502951448.2757 | 2369693.5412 | 2096267.3634
| Standard hour | (Mon-Sat) 4am - 9:30am, 11:30am - 5pm, 8pm - 10pm (Sunday) 4am - 10pm | 2170000 | kWh/year | Cost of equity* | 14% |  |  | NPV | 9436026765.5777 | 410262.0333 | 362924.1064
[5 empty] | WACC | 10.08% |  |  | Project payback period (years) | 5.4721 | 5.4721 | 5.4721
| Off-Peak hour | (Mon-Sun) 10pm - 4am | 725000 | kWh/year |  |  |  |  | LCOE - Levelized Cost of Energy (per kWh) | 1480.2938 | 0.064361 | 0.056934
| Peak hour | (Mon-Sat) 9:30am -11:30am, 5pm - 8pm | 1325000 | kWh/year | CAPEX Inputs
[5 empty] | Unit PV cost | 13800000 | VND/kWp | CAPEX Self-purchase with loan | Total Upfront Cost | -3726000000 | -162000 | -143307.6923
| Total Electricity Consumption |  | 4220000 | kWh/year | Total PV cost | 12420000000 | VND |  | Equity IRR | 27.76% | 27.76% | 27.76%
[5 empty] | Insurance cost | 0.25% | of total CAPEX/year |  | Average annual PV savings (expense) | 2009284461.7665 | 87360.194 | 77280.1716
| Rooftop & PV System Specifics |  |  |  | O&M | 115000 | VND/kWp/year |  | Total PV savings (expense) | 40185689235.3309 | 1747203.8798 | 1545603.4321
| Location of the roof (degrees lattitude) |  | Ho Chi Minh City (11° N) |  | Debt | 0.7 |  |  | NPV | 9968610504.8705 | 433417.848 | 383408.0963
| PV capacity to be installed on the roof |  | 900 | kWp | Equity | 30% |  |  | Project payback period (years) | 5.0227 | 5.0227 | 5.0227
| PV electricity exported to grid (in Net Billing) |  | 100% | % of consumable PV | Term | 8 | years
| PV output degradation (from panel aging) |  | 0.5% | /year | Amount of debt | 8694000000 | VND | OPEX / PPA Self-consumption | Upfront PV cost | 0 | 0 | 0
| PV system total output in year 1 |  | 0 | kWh/year | Amount of equity | 3726000000 | VND |  | Annual PV savings (expense) | 177859940.9563 | 7733.0409 | 6840.767
[9 empty] | Total PV savings (expense) | 3557198819.127 | 154660.8182 | 136815.3392
[5 empty] | OPEX Inputs |  |  |  | NPV - Net Present Value | 1371669391.1988 | 59637.7996 | 52756.515
[5 empty] | Price discount from EVN tariff | 5% |  |  | Project payback period | Day 1
[5 empty] | PPA net billing revenue retained* | 0%

## Tab 4. Financing Sensitivity (hidden)
Electric Tariff | Rate |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Standard (normal) | 1685 | VND/kWh |  | No PV System
Off-Peak | 1100 | VND/kWh |  | Electric Consumed
Peak | 3076 | VND/kWh |  | Standard Hour (kWh) |  | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000 | 2170000
Net-Billing Payment | 0 | VND/kWh |  | Peak Hour (kWh) |  | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000 | 1325000
Peak Period for PV | 3076 | VND/kWh |  | Off Peak Hour (kWh) |  | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000 | 725000
|  |  |  | Total (kWh) |  | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000
Installed Capacity | 900 | kWp
Standard PV Hours Portion of a Day | 0.75 |  |  | Retail Tariff
Peak PV Hours Portion of a Day | 0.25 |  |  | Standard Hour (VND/kWh) |  | 1685 | 1745.66 | 1808.5038 | 1873.6099 | 1941.0599 | 2010.938 | 2083.3318 | 2158.3317 | 2236.0317 | 2316.5288 | 2399.9238 | 2486.3211 | 2575.8287 | 2668.5585 | 2764.6266 | 2864.1531 | 2967.2627 | 3074.0841 | 3184.7511 | 3299.4022
PV System Output Year 1 | 1291680 | kWh/year |  | Peak Hour (VND/kWh) |  | 3076 | 3186.736 | 3301.4585 | 3420.311 | 3543.4422 | 3671.0061 | 3803.1623 | 3940.0762 | 4081.9189 | 4228.868 | 4381.1073 | 4538.8271 | 4702.2249 | 4871.505 | 5046.8792 | 5228.5668 | 5416.7952 | 5611.7998 | 5813.8246 | 6023.1223
PV Energy Consumed On-Site | 100% |  |  | Off Peak Hour (VND/kWh) |  | 1100 | 1139.6 | 1180.6256 | 1223.1281 | 1267.1607 | 1312.7785 | 1360.0385 | 1408.9999 | 1459.7239 | 1512.274 | 1566.7159 | 1623.1176 | 1681.5499 | 1742.0857 | 1804.8007 | 1869.7736 | 1937.0854 | 2006.8205 | 2079.066 | 2153.9124
EVN Tariff Escalation | 3.6%
CAPEX (per kWp) | 13800000 | VND/kWp |  | Electricity Expense
Total CAPEX | 12420000000 | VND |  | Standard Hour (VND) |  | 3656450000 | 3788082200 | 3924453159.2 | 4065733472.9312 | 4212099877.9567 | 4363735473.5632 | 4520829950.6114 | 4683579828.8335 | 4852188702.6715 | 5026867495.9676 | 5207834725.8225 | 5395316775.9521 | 5589548179.8863 | 5790771914.3623 | 5999239703.2793 | 6215212332.5974 | 6438959976.5709 | 6670762535.7274 | 6910909987.0136 | 7159702746.5461
PV Output Degradation | 0.5% | per year |  | Peak Hour (VND) |  | 4075700000 | 4222425200 | 4374432507.2 | 4531912077.4592 | 4695060912.2477 | 4864083105.0887 | 5039190096.8718 | 5220600940.3592 | 5408542574.2122 | 5603250106.8838 | 5804967110.7316 | 6013945926.718 | 6230447980.0798 | 6454744107.3627 | 6687114895.2277 | 6927851031.4559 | 7177253668.5883 | 7435634800.6575 | 7703317653.4812 | 7980637089.0065
Insurance Cost (of Total CAPEX) | 0.25% | per year |  | Off Peak Hour (VND) |  | 797500000 | 826210000 | 855953560 | 886767888.16 | 918691532.1338 | 951764427.2906 | 986027946.673 | 1021524952.7533 | 1058299851.0524 | 1096398645.6903 | 1135868996.9351 | 1176760280.8248 | 1219123650.9345 | 1263012102.3681 | 1308480538.0534 | 1355585837.4233 | 1404386927.5705 | 1454944856.9631 | 1507322871.8137 | 1561586495.199
O&M | 115000 | VND/kWp/year |  | Total Electricity Expense w/o RTS (VND) |  | 8529650000 | 8836717400 | 9154839226.4 | 9484413438.5504 | 9825852322.3382 | 10179583005.9424 | 10546047994.1563 | 10925705721.9459 | 11319031127.936 | 11726516248.5417 | 12148670833.4892 | 12586022983.4948 | 13039119810.9006 | 13508528124.093 | 13994835136.5604 | 14498649201.4766 | 15020600572.7297 | 15561342193.348 | 16121550512.3085 | 16701926330.7516
Inverter Replace | 1242000000 | VND/kWp
Inflation Rate | 4.5%
Corporate Tax | 20% |  |  | With PV System
|  |  |  | PV Energy Yield (kWh/year) |  | 1291680 | 1285221.6 | 1278795.492 | 1272401.5145 | 1266039.507 | 1259709.3094 | 1253410.7629 | 1247143.7091 | 1240907.9905 | 1234703.4506 | 1228529.9333 | 1222387.2837 | 1216275.3472 | 1210193.9705 | 1204143.0006 | 1198122.2856 | 1192131.6742 | 1186171.0158 | 1180240.1608 | 1174338.96
Debt | 70% |  |  | PV Energy for Self-Consumption (kWh/year) |  | 1291680 | 1285221.6 | 1278795.492 | 1272401.5145 | 1266039.507 | 1259709.3094 | 1253410.7629 | 1247143.7091 | 1240907.9905 | 1234703.4506 | 1228529.9333 | 1222387.2837 | 1216275.3472 | 1210193.9705 | 1204143.0006 | 1198122.2856 | 1192131.6742 | 1186171.0158 | 1180240.1608 | 1174338.96
Amount of Debt | 8694000000 | VND |  | Excess PV to EVN Grid (kWh/year) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Equity | 30%
Amount of Equity | 3726000000 | VND
Interest Rate | 10.5% |  |  | Electricity Savings and Revenue w/ PV System
Term | 8 |  |  | Standard Period Saved (VND) |  | 1632360600 | 1682669953.692 | 1734529841.6648 | 1787988051.3849 | 1843093843.1286 | 1899897995.3738 | 1958452851.5912 | 2018812368.4773 | 2081032165.6737 | 2145169577.0198 | 2211283703.3835 | 2279435467.1218 | 2349687668.2185 | 2422105042.153 | 2496754319.5522 | 2573704287.6808 | 2653025853.8271 | 2734792110.642 | 2819078403.492 | 2905962399.8877
|  |  |  | Peak Period Saved (VND) |  | 993301920 | 1023915485.1744 | 1055472560.4275 | 1088002224.7399 | 1121534453.3063 | 1156100145.1572 | 1191731151.631 | 1228460305.7242 | 1266321452.3467 | 1305349479.508 | 1345580350.4664 | 1387051136.8678 | 1429800052.9061 | 1473866490.5366 | 1519291055.775 | 1566115606.114 | 1614383289.0944 | 1664138582.0643 | 1715427333.1635 | 1768296803.5716
Cost of Equity | 14% |  |  | Net-billing Revenue (Untaxed) (VND) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risk Free Rate | 6% |  |  | Electricity Savings and Revenue (VND) |  | 2625662520 | 2706585438.8664 | 2790002402.0923 | 2875990276.1247 | 2964628296.4349 | 3055998140.531 | 3150184003.2222 | 3247272674.2015 | 3347353618.0204 | 3450519056.5278 | 3556864053.85 | 3666486603.9896 | 3779487721.1246 | 3895971532.6897 | 4016045375.3271 | 4139819893.7947 | 4267409142.9215 | 4398930692.7063 | 4534505736.6555 | 4674259203.4593
Market Risk Premium | 8%
WACC | 10.08%
WACC (Sensitivity) | 10.08%
Operating Costs of PV System
Total CAPEX | 12420000000 | VND | % of Total Investment | Insurance Cost (VND) |  | -31050000 | -32447250 | -33907376.25 | -35433208.1812 | -37027702.5494 | -38693949.1641 | -40435176.8765 | -42254759.836 | -44156224.0286 | -46143254.1099 | -48219700.5448 | -50389587.0693 | -52657118.4874 | -55026688.8194 | -57502889.8162 | -60090519.858 | -62794593.2516 | -65620349.9479 | -68573265.6956 | -71659062.6519
PV Panel | 7017300000 | VND | 56.5% | O&M Cost (VND) |  | -103500000 | -108157500 | -113024587.5 | -118110693.9375 | -123425675.1647 | -128979830.5471 | -134783922.9217 | -140849199.4532 | -147187413.4286 | -153810847.0329 | -160732335.1494 | -167965290.2311 | -175523728.2915 | -183422296.0646 | -191676299.3875 | -200301732.8599 | -209315310.8386 | -218734499.8264 | -228577552.3186 | -238863542.1729
Inverter | 1242000000 | VND | 10% | Total Cost (VND) |  | -134550000 | -140604750 | -146931963.75 | -153543902.1187 | -160453377.7141 | -167673779.7112 | -175219099.7982 | -183103959.2892 | -191343637.4572 | -199954101.1427 | -208952035.6942 | -218354877.3004 | -228180846.7789 | -238448984.884 | -249179189.2037 | -260392252.7179 | -272109904.0902 | -284354849.7743 | -297150818.0141 | -310522604.8248
Civil Balance of Plant | 2235600000 | VND | 18%
Electrical Balance of Plant | 869400000 | VND | 7%
Grid Connection | 310500000 | VND | 2.5% | Net Electricity Expense Saved (VND) | -12420000000 | 2491112520 | 2565980688.8664 | 2643070438.3423 | 2722446374.006 | 2804174918.7208 | 2888324360.8198 | 2974964903.424 | 3064168714.9124 | 3156009980.5632 | 3250564955.3851 | 3347912018.1558 | 3448131726.6892 | 3551306874.3457 | 3657522547.8057 | 3766866186.1234 | 3879427641.0768 | 3995299238.8313 | 4114575842.932 | 4237354918.6414 | 4363736598.6345
Development Costs | 621000000 | VND | 5%
Other | 124200000 | VND | 1%
| 12420000000 | VND | 100% | Depreciation
|  |  |  | Initial Depreciation Expense (VND) |  | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -558900000 | -558900000 | -558900000 | -558900000 | -558900000 | -558900000 | -558900000 | -558900000 | -558900000 | -558900000 | -558900000
|  |  |  | Inverter Replacement Cost (VND) | [10 empty] | -124200000 | -124200000 | -124200000 | -124200000 | -124200000 | -124200000 | -124200000 | -124200000 | -124200000 | -124200000 | -124200000
PV Lease |  |  |  | Total Depreciation Expense (VND) |  | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000
Pricing Discount Below EVN | 5%
Net-Billing Revenue Retained | 0%
Debt
Emissions |  |  |  | Beginning Principal O/S (VND) | 8694000000 | 8694000000 | 7947452511.986 | 7122517537.7305 | 6210964391.1782 | 5203698164.2379 | 4090668983.4689 | 2860771738.7191 | 1501735283.2706 | 0 | 0
EVN Electricity Emission Factor (tCO2/kWh) | 0.0008458 |  |  | Interest Repayment (VND) | 0 | 912870000 | 834482513.7585 | 747864341.4617 | 652151261.0737 | 546388307.245 | 429520243.2642 | 300381032.5655 | 157682204.7434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Principal Repayment (VND) | 0 | 746547488.014 | 824934974.2555 | 911553146.5523 | 1007266226.9403 | 1113029180.769 | 1229897244.7498 | 1359036455.4485 | 1501735283.2706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Total Repayment (VND) | 0 | 1659417488.014 | 1659417488.014 | 1659417488.014 | 1659417488.014 | 1659417488.014 | 1659417488.014 | 1659417488.014 | 1659417488.014 | 0 | 0
|  |  |  | Ending Principal O/S (VND) | 8694000000 | 7947452511.986 | 7122517537.7305 | 6210964391.1782 | 5203698164.2379 | 4090668983.4689 | 2860771738.7191 | 1501735283.2706 | 0 | 0 | 0
Taxes
|  |  |  | Net Savings (VND) |  | 2491112520 | 2565980688.8664 | 2643070438.3423 | 2722446374.006 | 2804174918.7208 | 2888324360.8198 | 2974964903.424 | 3064168714.9124 | 3156009980.5632 | 3250564955.3851 | 3347912018.1558 | 3448131726.6892 | 3551306874.3457 | 3657522547.8057 | 3766866186.1234 | 3879427641.0768 | 3995299238.8313 | 4114575842.932 | 4237354918.6414 | 4363736598.6345
|  |  |  | Depreciation (VND) | 0 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000 | -683100000
|  |  |  | Interest (VND) | 0 | -912870000 | -834482513.7585 | -747864341.4617 | -652151261.0737 | -546388307.245 | -429520243.2642 | -300381032.5655 | -157682204.7434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Net Tax Payment (No Loan) (VND) | 0 | 361602504 | 376576137.7733 | 391994087.6685 | 407869274.8012 | 424214983.7442 | 441044872.164 | 458372980.6848 | 476213742.9825 | 494581996.1126 | 513492991.077 | 532962403.6312 | 553006345.3378 | 573641374.8691 | 594884509.5611 | 616753237.2247 | 639265528.2154 | 662439847.7663 | 686295168.5864 | 710850983.7283 | 736127319.7269
|  |  |  | Net Tax Payment (w/ Loan) (VND) |  | 179028504 | 209679635.0216 | 242421219.3761 | 277439022.5865 | 314937322.2952 | 355140823.5111 | 398296774.1717 | 444677302.0338 | 494581996.1126 | 513492991.077 | 532962403.6312 | 553006345.3378 | 573641374.8691 | 594884509.5611 | 616753237.2247 | 639265528.2154 | 662439847.7663 | 686295168.5864 | 710850983.7283 | 736127319.7269
Net Cash Flows
|  |  |  | Net Project Cash Flow (CAPEX, No Loan) (VND) | -12420000000 | 2129510016 | 2189404551.0931 | 2251076350.6738 | 2314577099.2048 | 2379959934.9767 | 2447279488.6558 | 2516591922.7392 | 2587954971.9299 | 2661427984.4506 | 2737071964.308 | 2814949614.5247 | 2895125381.3514 | 2977665499.4765 | 3062638038.2445 | 3150112948.8987 | 3240162112.8615 | 3332859391.065 | 3428280674.3456 | 3526503934.9131 | 3627609278.9076
|  |  |  | Accumulated Cash Flow (CAPEX, No Loan) (VND | -12420000000 | -10290489984 | -8101085432.9069 | -5850009082.2331 | -3535431983.0283 | -1155472048.0516 | 1291807440.6042 | 3808399363.3434 | 6396354335.2733 | 9057782319.7239 | 11794854284.0319 | 14609803898.5566 | 17504929279.908 | 20482594779.3845 | 23545232817.629 | 26695345766.5278 | 29935507879.3892 | 33268367270.4542 | 36696647944.7999 | 40223151879.713 | 43850761158.6206
|  |  |  | Net Cash Flow to Equity (CAPEX w/ Loan) (VND) | -3726000000 | 652666527.986 | 696883565.8308 | 741231730.9521 | 785589863.4055 | 829820108.4116 | 873766049.2947 | 917250641.2383 | 960073924.8646 | 2661427984.4506 | 2737071964.308 | 2814949614.5247 | 2895125381.3514 | 2977665499.4765 | 3062638038.2445 | 3150112948.8987 | 3240162112.8615 | 3332859391.065 | 3428280674.3456 | 3526503934.9131 | 3627609278.9076
|  |  |  | Accumulated Cash Flow (CAPEX, w/ Loan) (VND) | -3726000000 | -3073333472.014 | -2376449906.1832 | -1635218175.2311 | -849628311.8255 | -19808203.4139 | 853957845.8808 | 1771208487.1191 | 2731282411.9836 | 5392710396.4342 | 8129782360.7423 | 10944731975.2669 | 13839857356.6183 | 16817522856.0948 | 19880160894.3394 | 23030273843.2381 | 26270435956.0996 | 29603295347.1646 | 33031576021.5102 | 36558079956.4233 | 40185689235.3309
Payback and LCOE Calculations
|  |  |  | Payback Period (Self-Financed) (Year) | [6 empty] | 5.4721
|  |  |  | Payback Period (w/ Loan) (Year) | [6 empty] | 5.0227
|  |  |  | Total Annual Expense (VND) |  | 496152504 | 517180887.7733 | 538926051.4185 | 561413176.9199 | 584668361.4583 | 608718651.8752 | 633592080.483 | 659317702.2716 | 685925633.5698 | 713447092.2197 | 741914439.3253 | 771361222.6382 | 801822221.6481 | 833333494.4451 | 865932426.4284 | 899657780.9333 | 934549751.8565 | 970650018.3607 | 1008001801.7424 | 1046649924.5517
|  |  |  | Total Annual Expense, Discounted (VND) |  | 450719934.593 | 426801193.8177 | 404020977.4611 | 382339280.1688 | 361715807.738 | 342110248.1054 | 323482502.3145 | 305792880.0771 | 289002264.0608 | 273072246.6009 | 257965242.143 | 243644578.3716 | 230074568.6653 | 217220568.2294 | 205049016.0079 | 193527464.24 | 182624597.3253 | 172310241.4732 | 162555366.4461 | 153332080.5593
|  |  |  | Energy Yield (kWh) |  | 1291680 | 1285221.6 | 1278795.492 | 1272401.5145 | 1266039.507 | 1259709.3094 | 1253410.7629 | 1247143.7091 | 1240907.9905 | 1234703.4506 | 1228529.9333 | 1222387.2837 | 1216275.3472 | 1210193.9705 | 1204143.0006 | 1198122.2856 | 1192131.6742 | 1186171.0158 | 1180240.1608 | 1174338.96
|  |  |  | Sum of Discounted Annual Expenses (VND) |  | 5577361058.3985
|  |  |  | Initial Investment Cost (VND) |  | 12420000000
|  |  |  | Sum of Energy Yield (kWh) |  | 24642546.9678
|  |  |  | LCOE (VND/kWh) |  | 1480.2938
Leasing option (OPEX)
|  |  |  | PV Energy Yield (kWh/year) |  | 1291680 | 1285221.6 | 1278795.492 | 1272401.5145 | 1266039.507 | 1259709.3094 | 1253410.7629 | 1247143.7091 | 1240907.9905 | 1234703.4506 | 1228529.9333 | 1222387.2837 | 1216275.3472 | 1210193.9705 | 1204143.0006 | 1198122.2856 | 1192131.6742 | 1186171.0158 | 1180240.1608 | 1174338.96
|  |  |  | PV Energy for Self-Consumption (kWh) |  | 1291680 | 1285221.6 | 1278795.492 | 1272401.5145 | 1266039.507 | 1259709.3094 | 1253410.7629 | 1247143.7091 | 1240907.9905 | 1234703.4506 | 1228529.9333 | 1222387.2837 | 1216275.3472 | 1210193.9705 | 1204143.0006 | 1198122.2856 | 1192131.6742 | 1186171.0158 | 1180240.1608 | 1174338.96
|  |  |  | PV Energy during Peak Hour (kWh) |  | 322920 | 321305.4 | 319698.873 | 318100.3786 | 316509.8767 | 314927.3274 | 313352.6907 | 311785.9273 | 310226.9976 | 308675.8626 | 307132.4833 | 305596.8209 | 304068.8368 | 302548.4926 | 301035.7502 | 299530.5714 | 298032.9186 | 296542.754 | 295060.0402 | 293584.74
|  |  |  | PV Energy during Standard Hour (kWh) |  | 968760 | 963916.2 | 959096.619 | 954301.1359 | 949529.6302 | 944781.9821 | 940058.0722 | 935357.7818 | 930680.9929 | 926027.5879 | 921397.45 | 916790.4627 | 912206.5104 | 907645.4779 | 903107.2505 | 898591.7142 | 894098.7557 | 889628.2619 | 885180.1206 | 880754.22
Discount against EVN Offered by Developer
|  |  |  | PV Lease Standard Tariff (VND/kWh) |  | 1600.75 | 1658.377 | 1718.0786 | 1779.9294 | 1844.0069 | 1910.3911 | 1979.1652 | 2050.4151 | 2124.2301 | 2200.7024 | 2279.9276 | 2362.005 | 2447.0372 | 2535.1306 | 2626.3953 | 2720.9455 | 2818.8995 | 2920.3799 | 3025.5136 | 3134.4321
|  |  |  | PV Lease Peak Tariff (VND/kWh) |  | 2922.2 | 3027.3992 | 3136.3856 | 3249.2955 | 3366.2701 | 3487.4558 | 3613.0042 | 3743.0724 | 3877.823 | 4017.4246 | 4162.0519 | 4311.8858 | 4467.1136 | 4627.9297 | 4794.5352 | 4967.1385 | 5145.9555 | 5331.2099 | 5523.1334 | 5721.9662
PV energy during Peak Hour (kWh)
|  |  |  | Peak Period Expense Saved (VND) |  | 49665096 | 51195774.2587 | 52773628.0214 | 54400111.237 | 56076722.6653 | 57805007.2579 | 59586557.5815 | 61423015.2862 | 63316072.6173 | 65267473.9754 | 67279017.5233 | 69352556.8434 | 71490002.6453 | 73693324.5268 | 75964552.7887 | 78305780.3057 | 80719164.4547 | 83206929.1032 | 85771366.6582 | 88414840.1786
|  |  |  | Standard Period Expense Saved (VND) |  | 81618030 | 84133497.6846 | 86726492.0832 | 89399402.5692 | 92154692.1564 | 94994899.7687 | 97922642.5796 | 100940618.4239 | 104051608.2837 | 107258478.851 | 110564185.1692 | 113971773.3561 | 117484383.4109 | 121105252.1077 | 124837715.9776 | 128685214.384 | 132651292.6914 | 136739605.5321 | 140953920.1746 | 145298119.9944
|  |  |  | Net-Billing with Profit Sharing (VND) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Total Electricity Expense Saved (VND) |  | 131283126 | 135329271.9433 | 139500120.1046 | 143799513.8062 | 148231414.8217 | 152799907.0266 | 157509200.1611 | 162363633.7101 | 167367680.901 | 172525952.8264 | 177843202.6925 | 183324330.1995 | 188974386.0562 | 194798576.6345 | 200802268.7664 | 206990994.6897 | 213370457.1461 | 219946534.6353 | 226725286.8328 | 233712960.173
|  |  |  | Cumulative Electricity Expense Saved (VND) | 0 | 131283126 | 266612397.9433 | 406112518.0479 | 549912031.8542 | 698143446.6759 | 850943353.7025 | 1008452553.8636 | 1170816187.5737 | 1338183868.4747 | 1510709821.3011 | 1688553023.9936 | 1871877354.193 | 2060851740.2493 | 2255650316.8838 | 2456452585.6501 | 2663443580.3399 | 2876814037.4859 | 3096760572.1212 | 3323485858.954 | 3557198819.127
|  |  |  | Emissions Reductions | Total
|  |  |  | Total Electricity Consumption (kWh) | 84400000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000 | 4220000
|  |  |  | PV Energy for Self-Consumption (kWh/year) | 24642546.9678 | 1291680 | 1285221.6 | 1278795.492 | 1272401.5145 | 1266039.507 | 1259709.3094 | 1253410.7629 | 1247143.7091 | 1240907.9905 | 1234703.4506 | 1228529.9333 | 1222387.2837 | 1216275.3472 | 1210193.9705 | 1204143.0006 | 1198122.2856 | 1192131.6742 | 1186171.0158 | 1180240.1608 | 1174338.96
|  |  |  | Total EVN Electricity Consumption w/ PV (kWh) | 59757453.0322 | 2928320 | 2934778.4 | 2941204.508 | 2947598.4855 | 2953960.493 | 2960290.6906 | 2966589.2371 | 2972856.2909 | 2979092.0095 | 2985296.5494 | 2991470.0667 | 2997612.7163 | 3003724.6528 | 3009806.0295 | 3015856.9994 | 3021877.7144 | 3027868.3258 | 3033828.9842 | 3039759.8392 | 3045661.04
|  |  |  | Emissions without PV (tCO2) | 71385.52
|  |  |  | Emissions with PV (tCO2) | 50542.8538
|  |  |  | Emissions Reductions (tCO2) | 20842.6662